{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":9,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXM-M"]
[]
[]
[]
[]
["","","","","","2MXM40M2V1B","2MXM40M4V1B","2MXM40M3V1B","2MXM50M2V1B"]
["Ventilator","Hitrost pretoka zraka","Hlajenje","Izjemno nizka","m³/min","30","","","34"]
["","","Ogrevanje","Izjemno nizka","m³/min","32","","","34"]
["","","","Izjemno nizka","cfm","1059","","","1200"]
["","","Ogrevanje","Izjemno nizka","cfm","1130","","","1200"]
["Mere","Enota","","Višina","mm","550","550","550","550"]
["","","","Širina","mm","765","765","765","765"]
["","","","Globina","mm","285","285","285","285"]
["Teža","Enota","","","kg","36","36","36","41"]
["Motor ventilatorja","Hitrost","Hlajenje","Izjwemno nizka","vrt/min","760","500","500","890"]
["","","Ogrevanje","Izjwemno nizka","vrt/min","820","320","320","890"]
["Kompresor","Tip","","","","Hermetično zaprt nihajni kompresor","Hermetično zaprt nihajni kompresor","Hermetično zaprt nihajni kompresor","Hermetično zaprt nihajni kompresor"]
["Območje delovanja","Hlajenje","Okolje","Min.","° CDB","-10","-10","-10 (2)","-10"]
["","","","Maks.","° CDB","46","46","46 (2)","46"]
["","Gretje","Okolje","Min.","° CWB","-15","-15","-15","-15"]
["","","","Maks.","° CWB","18","18","18","18"]
["Raven zvočnega tlaka","Hlajenje","","Visok","dBA","","46","46"]
["","","","Nom.","dBA","48","","","46"]
["","Gretje","","Visok","dBA","","48","48"]
["","","","Nom.","dBA","50","","","48"]
["Hladilno sredstvo","Tip","","","","R-32","R-32","R-32","R-32"]
["","Polnitev","","","kg","0.88","0.88","0.88","1.15"]
["","Polnjenje","","","tCO2Eq","0.6","0.60","0.59","0.8"]
["","GWP","","","","675","675","675","675"]
["Priključki napeljave","Dolžina cevi","Maks.","OU - IU","m","20","20","20 (1)","20"]
["","Dodatno polnjenje hladilnega sredstva","","","kg/m","0,02 (za dolžino napeljave nad 20m)","0,02 (za dolžino napeljave nad 20m)","0,02 (za dolžino napeljave nad 20m)","0,02 (za dolžino napeljave nad 20m)"]
["","Višinska razlika","IU - OU","Maks.","m","15","15.0","15.0","15"]
["","","IU - IU","Maks.","m","7.5","7.5","7.5","7.5"]
["","Skupna dolžina cevi","Sistem","Dejansko","m","30","30","30","30"]
["Standardni pripomočki","Installation manual","","","","Installation manual","1","1","1"]
["","Drain plug","","","","Drain plug","1","1","1"]
["","Screw bag","","","","Screw bag","1","1","1"]
["Napajanje","Faza","","","","1~","1~","1~","1~"]
["","Frekvenca","","","Hz","50","50","50","50"]
["","Napetost","","","V","220-240","220-230-240","220-230-240","220-240"]
["Opombe","","","","","","(1) - Za en prostor"]
["","","","","","","","(1) - Za en prostor"]
["","","","","","","","(2) - Glejte ločeno risbo za obratovalno območje"]
["Standardni pripomočki","Reducer assembly","","","","","","","1"]