{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":6,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EBLA-D3W17"]
[]
[]
[]
[]
["","","","","","EBLA16DA3W17"]
["Grelna kapaciteta","Nom.","","","kW","16.0 (1) (2)"]
["Hladilna kapaciteta","Nom.","","","kW","14.0 (3), 15.3 (4)"]
["Kapaciteta grelca","1. korak","","","kW","3"]
["Vhodna moč","Hlajenje","","Nom.","kW","4.58 (3), 3.24 (4)"]
["","Gretje","","Nom.","kW","3.53 (1), 4.56 (2)"]
["COP","","","","","4.53 (1), 3.51 (2)"]
["EER","","","","","3.06 (3), 4.74 (4)"]
["Mere","Enota","","Višina","mm","870"]
["","","","Širina","mm","1380"]
["","","","Globina","mm","460"]
["Teža","Enota","","","kg","149"]
["Ventilator","Hitrost pretoka zraka","Gretje","Visok","m³/min","85.0"]
["","","Hlajenje","Visok","m³/min","85.0"]
["Območje delovanja","Gretje","Stran vode","Min.","°C","15 (6)"]
["","","","Maks.","°C","60 (6)"]
["","Hlajenje","Okolje","Min.","°CDB","10"]
["","","","Maks.","°CDB","43"]
["","","Stran vode","Min.","°C","5"]
["","","","Maks.","°C","22"]
["","Vroča voda","Okolje","Min.","°CDB","-25"]
["","","","Maks.","°CDB","35"]
["","","Stran vode","Min.","°C","25"]
["","","","Maks.","°C","55 (6)"]
["Hladilno sredstvo","Tip","","","","R-32"]
["","GWP","","","","675"]
["","Polnitev","","","kg","3.80"]
["","Polnjenje","","","tCO2Eq","2.57"]
["Ogrevanje prostora","Izhod vode v povprečnem podnebju 55°C","Splošno","SCOP","","3.37"]
["","","","Razred učinkovitosti sezonskega ogrevanja prostora","","A++"]
["","Izhod vode v povprečnem podnebju 35°C","Splošno","SCOP","","4.69"]
["","","","Razred učinkovitosti sezonskega ogrevanja prostora","","A+++"]
["Razpon energetske učinkovitosti","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Komponenta kompresorja","Glavni napajalnik","","Faza","","3N~"]
["","","","Napetost","V","400"]
["Napajanje","Ime","","","","W1"]
["","Faza","","","","3~"]
["","Frekvenca","","","Hz","50"]
["","Napetost","","","V","400"]
["Opombe","","","","","(1) - Pogoji: Ta DB/WB 7° C/6° C - LWC 35° C (DT = 5° C)"]
["","","","","","(2) - Pogoji: Ta DB/WB 7° C/6° C - LWC 45° C (Dt=5° C)"]
["","","","","","(3) - Hlajenje: EW 12°C; LW 7°C; okoljski pogoji: 35°CDB"]
["","","","","","(4) - Hlajenje: EW 23°C; LW 18°C; okoljski pogoji: 35°CDB"]
["","","","","","(5) - V skladu z EN14825"]
["","","","","","(6) - Več podrobnosti preverite na risbi z obratovalnim razponom"]
["","","","","","(7) - Odvisno od tipa obratovalnega načina, glejte priročnik za namestitev."]