{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":19,"n_cols":9,"rows_kept":19,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EHBX-E9W / ERGA04-08EVA"]
[]
[]
[]
[]
["","","","","","EHBX08EA9W / ERGA06EAV3A","EHBX08EF9W / ERGA06EAV3A","EHBX08EA9W / ERGA08EAV3A","EHBX08EF9W / ERGA08EAV3A"]
["Grelna kapaciteta","Nom.","","","kW","6.00 (1), 5.90 (2)","6.00 (1), 5.90 (2)","7.50 (1), 7.80 (2)","7.50 (1), 7.80 (2)"]
["Hladilna kapaciteta","Nom.","","","kW","5.96 (1), 5.09 (2)","5.96 (1), 5.09 (2)","6.25 (1), 5.44 (2)","6.25 (1), 5.44 (2)"]
["Vhodna moč","Gretje","","Nom.","kW","1.24 (1), 1.69 (2)","1.24 (1), 1.69 (2)","1.63 (1), 2.23 (2)","1.63 (1), 2.23 (2)"]
["","Hlajenje","","Nom.","kW","1.06 (1), 1.55 (2)","1.06 (1), 1.55 (2)","1.16 (1), 1.73 (2)","1.16 (1), 1.73 (2)"]
["COP","","","","","4.85 (1), 3.50 (2)","4.85 (1), 3.50 (2)","4.60 (1), 3.50 (2)","4.60 (1), 3.50 (2)"]
["EER","","","","","5.61 (1), 3.28 (2)","5.61 (1), 3.28 (2)","5.40 (1), 3.14 (2)","5.40 (1), 3.14 (2)"]
["Ogrevanje prostora","Izhod vode v povprečnem podnebju 55°C","Splošno","SCOP","","3.27","3.27","3.3","3.3"]
["","","","Razred učinkovitosti sezonskega ogrevanja prostora","","A++","A++","A++","A++"]
["","Izhod vode v povprečnem podnebju 35°C","Splošno","SCOP","","4.52","4.52","4.61","4.61"]
["","","","Razred učinkovitosti sezonskega ogrevanja prostora","","A+++","A+++","A+++","A+++"]
["Razpon energetske učinkovitosti","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Opombe","","","","","(1) - 1. pogoj: hlajenje Ta 35 °C - LWE 18 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - 1. pogoj: hlajenje Ta 35 °C - LWE 18 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - 1. pogoj: hlajenje Ta 35 °C - LWE 18 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(1) - 1. pogoj: hlajenje Ta 35 °C - LWE 18 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(2) - 2. pogoj: hlajenje Ta 35 °C - LWE 7 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 45 °C (DT = 5 °C)","(2) - 2. pogoj: hlajenje Ta 35 °C - LWE 7 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 45 °C (DT = 5 °C)","(2) - 2. pogoj: hlajenje Ta 35 °C - LWE 7 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 45 °C (DT = 5 °C)","(2) - 2. pogoj: hlajenje Ta 35 °C - LWE 7 °C (DT = 5 °C); ogrevanje Ta DB/WB 7 °C/6 °C - LWC 45 °C (DT = 5 °C)"]