{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":87,"n_cols":8,"rows_kept":87,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERQ-AV1"]
[]
[]
[]
[]
["","","","","","ERQ100A7V1B","ERQ125A7V1B","ERQ140A7V1B"]
["Raven zvočnega tlaka","Gretje","","Nom.","dBA","","53","55"]
["","Hlajenje","","Nom.","dBA","","51","53"]
["Standardni pripomočki","Priročnik za namestitev","","","","","1","1"]
["","Priročnik za upravljanje","","","","","1","1"]
["Hladilno sredstvo","Charge","","","TCO2Eq","","8.4","8.4"]
["","GWP","","","","","2,087.5","2,087.5"]
["","Polnjenje","","","kg","","4.0","4.0"]
["","Tip","","","","","R-410A","R-410A"]
["Delovni doseg","Hlajenje","","Maks.","°CDB","","46","46"]
["","","","Min.","°CDB","","-5","-5"]
["","Gretje","","Maks.","° CWB","","15.5","15.5"]
["","","","Min.","° CWB","","-20","-20"]
["Hladilna kapaciteta","Nom.","","","kW","","14.0 (1)","15.5 (1)"]
["Priključki napeljave","Tekočina","","Zun. premer","mm","","9.52","9.52"]
["","","","Tip","","","Priklopni spoj","Priklopni spoj"]
["","Plin","","Zun. premer","mm","","15.9","19.1"]
["","","","Tip","","","Priklopni spoj","Varilna povezava"]
["","priključka","","OD","mm","","26x3","26x3"]
["","","","Količina","","","3","3"]
["Vhodna moč","Hlajenje","","Nom.","kW","","3.51 (1)","4.53 (1)"]
["Sound power level","Hlajenje","","Nom.","dBA","","67","69"]
["COP","","","","","4.56 (2)","4.15 (2)","3.94 (2)"]
["Mere","Enota","","Širina","mm","","900","900"]
["","","","Globina","mm","","320","320"]
["","","","Višina","mm","","1,345","1,345"]
["Teža","Enota","","","kg","","120","120"]
["Ventilator","Hitrost pretoka zraka","Gretje","Nom.","m³/min","","105","105"]
["","","Hlajenje","Nom.","m³/min","","106","106"]
["EER","","","","","3.99 (1)","3.99 (1)","3.42 (1)"]
["Grelna kapaciteta","Nom.","","","kW","","16.0 (2)","18.0 (2)"]
["Power supply","Faza","","","","","1N~","1N~"]
["","Frekvenca","","","Hz","","50","50"]
["","Ime","","","","","V1","V1"]
["","Napetost","","","V","","220-240","220-240"]
["Opombe","","","","","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB; zunanja temperatura 35° CDB; ekvivalentna dolžina cevi: 7,5m (horizontalno); nivojska razlika: 0m","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB; zunanja temperatura 35° CDB; ekvivalentna dolžina cevi: 7,5m (horizontalno); nivojska razlika: 0m","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB; zunanja temperatura 35° CDB; ekvivalentna dolžina cevi: 7,5m (horizontalno); nivojska razlika: 0m"]
["","","","","","(2) - Ogrevanje: Notranja temperatura 20° CDB; zunanja temperatura 7° CDB, 6° CWB; ekvivalentna dolžina cevi hladilnega sredstva: 7,5m, nivojska razlika: 0m","(2) - Ogrevanje: Notranja temperatura 20° CDB; zunanja temperatura 7° CDB, 6° CWB; ekvivalentna dolžina cevi hladilnega sredstva: 7,5m, nivojska razlika: 0m","(2) - Ogrevanje: Notranja temperatura 20° CDB; zunanja temperatura 7° CDB, 6° CWB; ekvivalentna dolžina cevi hladilnega sredstva: 7,5m, nivojska razlika: 0m"]
["","","","","","","(3) - Nivo tlaka zvoka je relativna vrednost, odvisna od oddaljenosti in akustike okolja. Za več informacij, prosimo poglejte skice o nivojih zvoka.","(3) - Nivo tlaka zvoka je relativna vrednost, odvisna od oddaljenosti in akustike okolja. Za več informacij, prosimo poglejte skice o nivojih zvoka."]
["","","","","","","(4) - Zvočne vrednosti se merijo v prostoru izoliranem od odmeva.","(4) - Zvočne vrednosti se merijo v prostoru izoliranem od odmeva."]
["","","","","","","(5) - RLA temelji na naslednjih pogojih: Notranja temperatura 27° CDB, 19° CWB; zunanja temperatura 35° CDB","(5) - RLA temelji na naslednjih pogojih: Notranja temperatura 27° CDB, 19° CWB; zunanja temperatura 35° CDB"]
["","","","","","","(6) - Razpon napetosti: enote so primerne za uporabo na električnih sistemih, kjer napetost, dovajana na terminal enote ni izven navedenih omejitev.","(6) - Razpon napetosti: enote so primerne za uporabo na električnih sistemih, kjer napetost, dovajana na terminal enote ni izven navedenih omejitev."]
["","","","","","","(7) - Najvišje dopustno napetostno odstopanje med fazama je 2 %.","(7) - Najvišje dopustno napetostno odstopanje med fazama je 2 %."]
["","","","","","","(8) - Izberite velikost žice na podlagi vrednosti MCA","(8) - Izberite velikost žice na podlagi vrednosti MCA"]
["","","","","","","(9) - Namesto varovalke uporabite prekinjalo tokokroga. MFA se uporablja za izbiro prekinjala tokokroga in prekinjalo toka pri napaki ozemljitve (prekinjalo kroga ozemljitvenega uhajajočega toka).","(9) - Namesto varovalke uporabite prekinjalo tokokroga. MFA se uporablja za izbiro prekinjala tokokroga in prekinjalo toka pri napaki ozemljitve (prekinjalo kroga ozemljitvenega uhajajočega toka)."]
["","","","","","","(10) - MSC pomeni maksimalni tok med zagonom kompresorja","(10) - MSC pomeni maksimalni tok med zagonom kompresorja"]
["","","","","","","(11) - Oprema je skladna z EN 61000-3-12: Evropski/mednarodni tehnični standard, ki postavlja omejitve za harmonske tokove, ki jih proizvaja oprema, priklopljena na javni nizkonapetostni sistem z vhodnimi tokovi >16A in ≤ 75A na fazo","(11) - Oprema je skladna z EN 61000-3-12: Evropski/mednarodni tehnični standard, ki postavlja omejitve za harmonske tokove, ki jih proizvaja oprema, priklopljena na javni nizkonapetostni sistem z vhodnimi tokovi >16A in ≤ 75A na fazo"]
["","","","","","","(12) - Ssc: Kratkostična moč","(12) - Ssc: Kratkostična moč"]
["","","","","","","(13) - Vsebuje fluorirane toplogredne pline","(13) - Vsebuje fluorirane toplogredne pline"]
["Hladilna kapaciteta","Nom.","","","kW","11.2 (1)"]
["Grelna kapaciteta","Nom.","","","kW","12.5 (2)"]
["Vhodna moč","Hlajenje","","Nom.","kW","2.81 (1)"]
["","Gretje","","Nom.","kW","2.74 (2)"]
["Mere","Enota","","Višina","mm","1345"]
["","","","Širina","mm","900"]
["","","","Globina","mm","320"]
["Teža","Enota","","","kg","120"]
["Ventilator","Hitrost pretoka zraka","Hlajenje","Nom.","m³/min","106"]
["","","Gretje","Nom.","m³/min","102"]
["Del. doseg","Hlajenje","","Min.","°CDB","-5"]
["","","","Maks.","°CDB","46"]
["Območje delovanja","Gretje","","Min.","° CWB","-20"]
["","","","Maks.","° CWB","15.5"]
["Raven zvočne moči","Hlajenje","","Nom.","dBA","66"]
["Raven zvočnega tlaka","Hlajenje","","Nom.","dBA","50"]
["","Gretje","","Nom.","dBA","52"]
["Hladilno sredstvo","Tip","","","","R-410A"]
["","Polnitev","","","kg","4"]
["","Polnjenje","","","tCO2Eq","8.4"]
["","GWP","","","","2087.5"]
["Priključki cevne napeljave","Tekočina","","Tip","","Priklopni spoj"]
["","","","Zun. premer","mm","9.52"]
["","Plin","","Tip","","Priklopni spoj"]
["","","","Zun. premer","mm","15.9"]
["Priključki napeljave","priključka","","Količina","","3"]
["","","","OD","mm","26x3"]
["Standardni pripomočki","Installation manual","","","","1"]
["","Operation manual","","","","1"]
["Napajanje","Ime","","","","V1"]
["","Faza","","","","1N~"]
["","Napajanje-=-Frekvenca","","Frekvenca","","50"]
["","Napajanje-=-Napetost","","Napetost","","220-240"]
["Standardni pripomočki","Priključne cevi","","","","","","3"]