{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":13,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWE-DATN5V3-L"]
[]
[]
[]
[]
["","","","","","FWE03DATN5V3-L","FWE04DATN5V3-L","FWE05DATN5V3-L","FWE06DATN5V3-L","FWE07DATN5V3-L","FWE08DATN5V3-L","FWE10DATN5V3-L","FWE11DATN5V3-L"]
["Raven zvočnega tlaka","Nizko","","","dBA","21.0","23.0","27.0","29.0","24.0","24.0","33.0","34.0"]
["","Visok","","","dBA","35.0","34.0","40.0","40.0","40.0","40.0","47.0","49.0"]
["Standardni pripomočki","Priročnik za namestitev","","","","1","1","1","1","1","1","1","1"]
["Skupna raven zvočne moči","Nizko","","","dBA","32.0","34.0","37.0","39.0","34.0","34.0","43.0","44.0"]
["","Visoko","","","dBA","45.0","44.0","50.0","50.0","50.0","50.0","57.0","59.0"]
["Tok vode","Hlajenje","","Nizko","l/h","210","241","282","345","415","477","534","583"]
["","","","Visoko","l/h","334","354","443","536","589","674","897","962"]
["","Ogrevanje","","Visoko","l/h","344","409","496","689","751","797","1,029","1,092"]
["","","","Nizko","l/h","230","306","341","505","542","613","669","717"]
["","Padec vodnega tlaka","Ogrevanje","Visoko","kPa","18.59","15.05","22.22","16.99","36.92","28.69","45.14","50.28"]
["","","","Nizko","kPa","8.52","8.33","10.38","8.65","19.91","18.19","21.14","23.85"]
["","","Hlajenje","Visoko","kPa","13.18","10.09","14.35","8.85","13.48","18.67","29.00","33.09"]
["","","","Nizko","kPa","6.05","5.00","5.53","3.23","5.96","10.90","11.07","13.00"]
["Priključki napeljave","priključka","","OD","mm","17.3","17.3","17.3","17.3","17.3","17.3","17.3","17.3"]
["","Voda","","Dovod","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Odvod","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Vhodna moč","Visoko","","","kW","0.033","0.032","0.039","0.062","0.067","0.067","0.104","0.110"]
["","Nizko","","","kW","0.026","0.028","0.029","0.043","0.037","0.037","0.036","0.039"]
["Dovoljena temperatura vode","Ogrevanje","","Maks.","°C","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000"]
["","","","Min.","°C","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00"]
["","Hlajenje","","Min.","°C","5","5","5","5","5","5","5","5"]
["","","","Maks.","°C","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0"]
["Mere","Enota","","Širina","mm","795","795","795","995","1,195","1,195","1,195","1,195"]
["","","","Globina","mm","610","610","610","610","610","610","610","610"]
["","","","Višina","mm","200","200","200","200","200","200","200","200"]
["Ohišje","Barva","","","","Kovina","Kovina","Kovina","Kovina","Kovina","Kovina","Kovina","Kovina"]
["Teža","Enota","","","kg","17.5","18.5","18.5","22.0","25.5","25.5","25.5","25.5"]
["Ventilator","Hitrost pretoka zraka","","Nizko","m³/h","235","263","304","446","481","481","555","619"]
["","","","Visok","m³/h","407","385","488","677","725","725","1,032","1,116"]
["","Razpoložljivi statični pritisk","","Visoko","Pa","55","57","55","60","60","60","63","65"]
["","","","Nizko","Pa","27","33","32","41","34","34","32","34"]
["Power supply","Tip","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Faza","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frekvenca","","","Hz","50","50","50","50","50","50","50","50"]
["","Napetost","","","V","230","230","230","230","230","230","230","230"]
["Opombe","","","","","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB","(1) - Vstopna/izstopna temperatura vode 7/12 °C; temperatura vstopnega zraka 27 °C DB 19 °C WB"]
["","","","","","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K."]
["","","","","","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K."]