{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":10,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWH-AF"]
[]
[]
[]
[]
["","","","","","FWH02AAFN6V3","FWH03AAFN6V3","FWH04AAFN6V3","FWH06AAFN6V3","FWH08AAFN6V3"]
["Zmogljivost hlajenja (standardni pogoji)","Občutna zmogljivost 4-cevi","","Nizko","kW","1.24 (1)","1.49 (1)","2.00 (1)","3.47 (1)","4.29 (1)"]
["","","","Visoko","kW","1.94 (1)","3.38 (1)","3.02 (1)","5.81 (1)","6.98 (1)"]
["","Skupna zmogljivost 4-cevi","","Nizko","kW","1.56 (1)","2.01 (1)","2.58 (1)","4.73 (1)","5.83 (1)"]
["","","","Visoko","kW","2.35 (1)","3.38 (1)","3.62 (1)","7.45 (1)","9.00 (1)"]
["Zmogljivost ogrevanja (standardni pogoji)","Zmogljivost 4-cevi","","Nizko","kW","2.53 (3)","2.75 (3)","3.67 (3)","7.20 (3)","8.64 (3)"]
["","","","Visoko","kW","3.55 (3)","4.22 (3)","4.81 (3)","10.60 (3)","12.40 (3)"]
["Vhodna moč","Nizko","","","kW","0.018","0.032","0.057","0.047","0.064"]
["","Visoko","","","kW","0.042","0.050","0.089","0.108","0.147"]
["Mere","Enota","","Višina","mm","298","298","298","350","350"]
["","","","Širina","mm","577","577","577","793","793"]
["","","","Globina","mm","577","577","577","793","793"]
["Teža","Enota","","","kg","23.0","23.0","23.0","43.0","43.0"]
["Okrasna plošča","Mere","Enota","Višina","mm","41","41","41","75","75"]
["","","","Širina","mm","730","730","730","860","860"]
["","","","Globina","mm","730","730","730","860","860"]
["Ventilator","Hitrost pretoka zraka","","Nizko","m³/h","289","306","479","718","902"]
["","","","Visok","m³/h","533","640","805","1,380","1,651"]
["Skupna raven zvočne moči","Nizko","","","dBA","33.0 (4)","40.0 (4)","47.0 (4)","35.0 (4)","40.0 (4)"]
["","Visoko","","","dBA","45.0 (4)","50.0 (4)","58.0 (4)","51.0 (4)","56.0 (4)"]
["Raven zvočnega tlaka","Nizko","","","dBA","25.0 (4)","32.0 (4)","39.0 (4)","27.0 (4)","32.0 (4)"]
["","Visok","","","dBA","37.0 (4)","42.0 (4)","50.0 (4)","43.0 (4)","48.0 (4)"]
["Tok vode","Hlajenje","","Nizko","l/h","271 (1)","351 (1)","453 (1)","822 (1)","1,010 (1)"]
["","","","Visoko","l/h","410 (1)","589 (1)","637 (1)","1,299 (1)","1,571 (1)"]
["","Ogrevanje","","Visoko","l/h","311 (3)","369 (3)","421 (3)","929 (3)","1,083 (3)"]
["","","","Nizko","l/h","222 (3)","241 (3)","322 (3)","634 (3)","757 (3)"]
["","Padec vodnega tlaka","Hlajenje","Nizko","kPa","3 (1)","10 (1)","5 (1)","10 (1)","10 (1)"]
["","","","Visoko","kPa","6 (1)","22 (1)","9 (1)","252 (1)","34 (1)"]
["","","Ogrevanje","Nizko","kPa","4 (3)","6 (3)","5 (3)","12 (3)","16 (3)"]
["","","","Visoko","kPa","8 (3)","12 (3)","9 (3)","23 (3)","30 (3)"]
["Dovoljena temperatura vode","Hlajenje","","Min.","°C","5","5","5","5","5"]
["","Ogrevanje","","Maks.","°C","80","80","80","80","80"]
["Priključki napeljave","Voda","","Dovod","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\""]
["","","","Odvod","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\""]
["","priključka","","OD","mm","10","10","10","10","10"]
["Vodni priključki","Primarna tuljava","","","palcev","1/2\"","1/2\"","1/2\"","3/4 \"","3/4 \""]
["","Dodatna tuljava","","","palcev","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["Krmilni sistemi","Wired remote control","","","","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Tip","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Faza","","","","1~","1~","1~","1~","1~"]
["","Frekvenca","","","Hz","50","50","50","50","50"]
["","Napetost","","","V","230","230","230","230","230"]
["Opombe","","","","","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K."]
["","","","","","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K."]
["","","","","","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K."]
["","","","","","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741"]
["","","","","","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote."]