{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":11,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWH-AT"]
[]
[]
[]
[]
["","","","","","FWH02AATN6V3","FWH03AATN6V3","FWH04AATN6V3","FWH07AATN6V3","FWH06AATN6V3","FWH08AATN6V3"]
["Zmogljivost hlajenja (standardni pogoji)","Občutna zmogljivost 2-cevi","","Nizko","kW","1.33 (1)","1.66 (1)","2.43 (1)","3.68 (1)","3.42 (1)","4.59 (1)"]
["","","","Visoko","kW","2.14 (1)","3.18 (1)","3.79 (1)","6.10 (1)","5.29 (1)","7.35 (1)"]
["","Skupna zmogljivost 2-cevi","","Nizko","kW","1.70 (1)","2.39 (1)","3.40 (1)","5.16 (1)","4.64 (1)","6.34 (1)"]
["","","","Visoko","kW","2.53 (1)","4.31 (1)","5.00 (1)","8.24 (1)","7.01 (1)","9.73 (1)"]
["Zmogljivost ogrevanja (standardni pogoji)","Zmogljivost 2-cevi","","Nizko","kW","1.97 (2)","2.29 (2)","3.49 (2)","5.22 (2)","5.16 (2)","6.71 (2)"]
["","","","Visoko","kW","3.10 (2)","4.30 (2)","5.35 (2)","9.18 (2)","8.17 (2)","11.10 (2)"]
["Vhodna moč","Nizko","","","kW","0.018","0.032","0.057","0.047","0.047","0.064"]
["","Visoko","","","kW","0.042","0.050","0.089","0.108","0.108","0.147"]
["Mere","Enota","","Višina","mm","298","298","298","350","350","350"]
["","","","Širina","mm","577","577","577","793","793","793"]
["","","","Globina","mm","577","577","577","793","793","793"]
["Teža","Enota","","","kg","23.0","23.0","23.0","43.0","43.0","43.0"]
["Okrasna plošča","Mere","Enota","Višina","mm","41","41","41","75","75","75"]
["","","","Širina","mm","730","730","730","860","860","860"]
["","","","Globina","mm","730","730","730","860","860","860"]
["Ventilator","Hitrost pretoka zraka","","Nizko","m³/h","297","306","479","718","801","902"]
["","","","Visok","m³/h","557","640","805","1,380","1,494","1,651"]
["Skupna raven zvočne moči","Nizko","","","dBA","33.0 (4)","40.0 (4)","47.0 (4)","35.0 (4)","35.0 (4)","40.0 (4)"]
["","Visoko","","","dBA","45.0 (4)","50.0 (4)","58.0 (4)","51.0 (4)","51.0 (4)","56.0 (4)"]
["Raven zvočnega tlaka","Nizko","","","dBA","25.0 (4)","32.0 (4)","39.0 (4)","27.0 (4)","27.0 (4)","32.0 (4)"]
["","Visok","","","dBA","37.0 (4)","42.0 (4)","50.0 (4)","43.0 (4)","43.0 (4)","48.0 (4)"]
["Tok vode","Hlajenje","","Nizko","l/h","295 (1)","416 (1)","593 (1)","893 (1)","805 (1)","1,097 (1)"]
["","","","Visoko","l/h","441 (1)","749 (1)","873 (1)","1,434 (1)","1,223 (1)","1,696 (1)"]
["","Ogrevanje","","Visoko","l/h","539 (2)","747 (2)","930 (2)","1,596 (2)","1,420 (2)","1,930 (2)"]
["","","","Nizko","l/h","342 (2)","399 (2)","607 (2)","908 (2)","897 (2)","1,167 (2)"]
["","Padec vodnega tlaka","Hlajenje","Nizko","kPa","3 (1)","9 (1)","9 (1)","12 (1)","14 (1)","16 (1)"]
["","","","Visoko","kPa","6 (1)","26 (1)","18 (1)","26 (1)","28 (1)","32 (1)"]
["","","Ogrevanje","Nizko","kPa","3 (2)","7 (2)","8 (2)","10 (2)","14 (2)","15 (2)"]
["","","","Visoko","kPa","8 (2)","22 (2)","17 (2)","26 (2)","30 (2)","33 (2)"]
["Dovoljena temperatura vode","Hlajenje","","Min.","°C","5","5","5","5","5","5"]
["","Ogrevanje","","Maks.","°C","80","80","80","80","80","80"]
["Priključki napeljave","Voda","","Dovod","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\""]
["","","","Odvod","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\""]
["","priključka","","OD","mm","10","10","10","10","10","10"]
["Vodni priključki","Primarna tuljava","","","palcev","1/2\"","1/2\"","1/2\"","3/4 \"","3/4 \"","3/4 \""]
["Krmilni sistemi","Wired remote control","","","","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Tip","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Faza","","","","1~","1~","1~","1~","1~","1~"]
["","Frekvenca","","","Hz","50","50","50","50","50","50"]
["","Napetost","","","V","230","230","230","230","230","230"]
["Opombe","","","","","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K."]
["","","","","","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K."]
["","","","","","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K."]
["","","","","","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741"]
["","","","","","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote."]