{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":9,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWI-AF"]
[]
[]
[]
[]
["","","","","","FWI02AAFN6V3","FWI04AAFN6V3","FWI06AAFN6V3","FWI08AAFN6V3"]
["Zmogljivost hlajenja (standardni pogoji)","Občutna zmogljivost 4-cevi","","Nizko","kW","1.46 (1)","2.10 (1)","3.34 (1)","4.50 (1)"]
["","","","Visoko","kW","2.23 (1)","3.58 (1)","5.03 (1)","7.56 (1)"]
["","Skupna zmogljivost 4-cevi","","Nizko","kW","1.85 (1)","2.62 (1)","4.61 (1)","6.09 (1)"]
["","","","Visoko","kW","2.60 (1)","4.41 (1)","6.61 (1)","9.50 (1)"]
["Zmogljivost ogrevanja (standardni pogoji)","Zmogljivost 4-cevi","","Nizko","kW","2.90 (3)","3.73 (3)","7.01 (3)","8.96 (3)"]
["","","","Visoko","kW","3.86 (3)","5.51 (3)","9.53 (3)","12.90 (3)"]
["Vhodna moč","Nizko","","","kW","0.007","0.009","0.014","0.025"]
["","Visoko","","","kW","0.018","0.067","0.036","0.150"]
["Mere","Enota","","Višina","mm","298","298","350","350"]
["","","","Širina","mm","577","577","793","793"]
["","","","Globina","mm","577","577","793","793"]
["Teža","Enota","","","kg","23.0","23.0","43.0","43.0"]
["Okrasna plošča","Mere","Enota","Višina","mm","41","41","75","75"]
["","","","Širina","mm","730","730","860","860"]
["","","","Globina","mm","730","730","860","860"]
["Ventilator","Hitrost pretoka zraka","","Nizko","m³/h","356","395","687","956"]
["","","","Visok","m³/h","610","982","1,137","1,823"]
["Skupna raven zvočne moči","Nizko","","","dBA","35.0 (4)","38.0 (4)","35.0 (4)","43.0 (4)"]
["","Visoko","","","dBA","46.0 (4)","61.0 (4)","45.0 (4)","58.0 (4)"]
["Raven zvočnega tlaka","Nizko","","","dBA","35.0 (4)","38.0 (4)","35.0 (4)","43.0 (4)"]
["","Visok","","","dBA","46.0 (4)","61.0 (4)","45.0 (4)","58.0 (4)"]
["Tok vode","Hlajenje","","Nizko","l/h","317 (1)","451 (1)","792 (1)","1,045 (1)"]
["","","","Visoko","l/h","447 (1)","759 (1)","1,135 (1)","1,631 (1)"]
["","Ogrevanje","","Visoko","l/h","338 (3)","474 (3)","834 (3)","1,133 (3)"]
["","","","Nizko","l/h","254 (3)","321 (3)","613 (3)","785 (3)"]
["","Padec vodnega tlaka","Hlajenje","Nizko","kPa","4 (1)","7 (1)","12 (1)","17 (1)"]
["","","","Visoko","kPa","8 (1)","25 (1)","22 (1)","37 (1)"]
["","","Ogrevanje","Nizko","kPa","6 (3)","4 (3)","11 (3)","18 (3)"]
["","","","Visoko","kPa","11 (3)","11 (3)","19 (3)","33 (3)"]
["Dovoljena temperatura vode","Hlajenje","","Min.","°C","5","5","5","5"]
["","Ogrevanje","","Maks.","°C","80","80","80","80"]
["Priključki napeljave","Voda","","Dovod","","1/2\"","1/2\"","3/4\"","3/4\""]
["","","","Odvod","","1/2\"","1/2\"","3/4\"","3/4\""]
["","priključka","","OD","mm","10","10","10","10"]
["Vodni priključki","Primarna tuljava","","","palcev","1/2\"","1/2\"","3/4 \"","3/4 \""]
["","Dodatna tuljava","","","palcev","1/2\"","1/2\"","1/2\"","1/2\""]
["Krmilni sistemi","Wired remote control","","","","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Tip","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Faza","","","","1~","1~","1~","1~"]
["","Frekvenca","","","Hz","50","50","50","50"]
["","Napetost","","","V","230","230","230","230"]
["Opombe","","","","","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K.","(1) - Hlajenje: Notranja temperatura 27° CDB, 19° CWB, vstopna temperatura vode 7° C, dvig temperature vode 5K."]
["","","","","","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K.","(2) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 45°C, padec temperature vode 5K."]
["","","","","","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K.","(3) - Ogrevanje: notranja temp. 20°CDB, 15°CWB; vhodna temperatura vode 65°C, padec temperature vode 10K."]
["","","","","","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741","(4) - Raven zvočne moči po ISO3741"]
["","","","","","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote.","(5) - Raven zvočnega tlaka je merjena z mikrofonom, postavljenim na razdalji 1 m od enote."]